## Slide 1: Networking (related) Challenges for the Smart Grid
Jim Kurose
Department of Computer Science
University of Massachusetts
Amherst MA USA
IIT Mumbai, January 2013

## Slide 2: Overview
yesterday’s, today’s and tomorrow’s electric grid: a networking perspective
five (networking) smart grid challenges
  richer data gathering and distribution architecture
  monitoring, measurement
  dealing with demand: network-inspired approaches
  security and privacy
  power routing
grid v. Internet: similarities and dis-similarities
  reflections on Keshav’s 1st and 2nd hypotheses
This talk: part tutorial, part research, part speculation

## Slide 3: A word on my background …
power grid networks
computer networks
+
= ?
joint IITB/UMass smart grid
reading seminar

## Slide 4: Overview
yesterday’s, today’s and tomorrow’s electric grid: a networking perspective
five (networking) smart grid challenges
  ultra-reliable, multi-destination transport
  monitoring, measurement
  security and privacy
  dealing with demand: network-inspired approaches
  power routing
grid v. Internet: similarities and dis-similarities
  reflections on Keshav’s 1st and 2nd hypotheses

## Slide 5: The electric grid: structure (US-centric)
transmission network
(backbone)
distribution
network (edge)
power
sources
inter-connected regional
transmission network operators (RTOs)
edge (distribution)
networks
power
consumers
distributed
generation (DG)
Mesh transmission network
hierarchical
distribution network

## Slide 6: The electric grid: structure (US-centric)
electricity flows from producers to consumers
overall supply must equal demand, flowing over links of given capacity
  brownouts, blackouts
using ICT to efficiently, reliably, flexibly and sustainably monitor and control the generation, distribution and use of electricity
smart grid

## Slide 7: Selected smart grid applications
∂
∂
∂∂
∂∂∂
∂∂∂
∂∂∂

## Slide 8: SG applications: communication requirements
Bakken, D.E.; Bose, A.; Hauser, C.H.; Whitehead, D.E.; Zweigle, G.C., “Smart Generation and Transmission With Coherent, Real-Time Data,” Proceedings of the IEEE, 99(6), 2011

## Slide 9: The smart grid: communication flows
transmission network
(backbone)
distribution
network (edge)
distribution
network
operator(s)
regional
transmission
operator(s)
large-scale
electricity
generators
demand/
response
smart
scheduling, AMI
distributed
generation
monitoring
control
Monitoring, control
monitoring, control

## Slide 10: Grid communication network topology: from hierarchical to mesh topologies
Electricity flow (distribution network)
Data communication flow between control room, substations and field devices
Focus: “ enhancing the distributed control signaling architecture such that some level of device collaboration can be performed even when there are losses of control capability from the still dominant hierarchical control system
architecture.”
T.M. Overman and R.W. Sackman, "High Assurance Smart Grid: Smart Grid Control Systems Communications Architecture," 2010 SmartGridComm, 2010.

## Slide 11: Today’s grid control architecture: SCADA
supervisory control & data acquisition
centralized industrial measurement/control system:
  master terminal unit (MTU)
  remote terminal units (RTUs): data gathering, control units, polled by MTU
SCADA protocols: often proprietary, sometimes open
    DNP3: point-to-point link-layer polling protocol: addressing multiplexing, fragmentation, error checking/retrans, link control, prioritization
    DNP3: can poll over TCP/IP
MTU
RTU
RTU
RTUs

## Slide 12: Smart grid communication and the Internet
grid communication:
  stringent reliability, delay requirements for control
Internet: “best effort” service model
  network layer (IP):
    “best effort” to deliver packet between hosts, but no promises
    unreliable host-host delivery
    no delay guarantees
  transport layer (TCP): “laid back” transmission: “send … data in segments at its own convenience.” [RFC 793]
  transport layer (UDP): unreliable datagram transfer between

## Slide 13: Smart grid communication and the Internet
grid communication:
  stringent reliability, delay requirements for control
Internet: “best effort” service model
  network layer (IP):
    “best effort” to deliver packet between hosts, but no promises
    unreliable host-host delivery
    no delay guarantees
  transport layer (TCP): “laid back” transmission: “send … data in segments at its own convenience.” [RFC 793]
  transport layer (UDP): unreliable datagram transfer between
Internet’s traditional best effort delivery, transport protocols not well-suited for high assurance grid communication (but that doesn’t mean they can’t be fixed or used!)

## Slide 14
How can we, as networking researchers and computer scientists
inform design, analysis of smart grid communications

## Slide 15: Overview
yesterday’s, today’s and tomorrow’s electric grid: a networking perspective
five (networking) smart grid challenges
  richer data gathering and distribution architecture
  monitoring, measurement
  security and privacy
  dealing with demand: network-inspired approaches
  power routing
grid v. Internet: similarities and dis-similarities
  reflections on Keshav’s 1st and 2nd hypotheses

## Slide 16
  smart grid: many data sources and sink with interests in subsets of data:
    real-time control, data analytics, archiving
1. Rich data gathering, distribution architecture
  SCADA: simple centralized polling
  richer communication paradigms:
    self-healing mesh network
    QoS bandwidth, delay guarantees
    multicast (1-many)
    higher-level abstractions (pub-sub, e.g., Gridstat)

## Slide 17
Challenge: self healing, multicast mesh
multicast
QoS tree
X
multicast
QoS tree
healed

## Slide 18
Challenge: self healing, multicast mesh
  Multicast QoS: path reservation, as in MPLS
  compute source-specific multicast trees, with known link bandwidths and source-to-destination traffic rates
    different from public Internet, which has unknown demand
  compute backup multicast trees
    offline, in case of each link failure scenario
    minimize # affected hosts, or # affected routers
multicast
QoS tree
X
multicast
QoS tree
healed

## Slide 19
Challenge: self healing, multicast mesh
  Down link, packet loss detection:
  in-network, per-link measurement, monitoring of link flows
  rapid, local link,/flow failure detection
  installation of pre-computed backup multicast forwarding trees
multicast
QoS tree
X
multicast
QoS tree
healed
This requires changes to existing routers ….. how?

## Slide 20: Openflow: open network control plane
Custom Hardware
protocol
protocol
Custom Hardware
Custom Hardware
Custom Hardware
Custom Hardware
Operating
System
Operating
System
Operating
System
Operating
System
Operating
System
Network OS
protocol
protocol
protocol
protocol
protocol
protocol
protocol
protocol
protocol
protocol

## Slide 21: Openflow: open smart grid control plane
Custom Hardware
Custom Hardware
Custom Hardware
Custom Hardware
Custom Hardware
Network OS
Smart grid protocol
protocol

## Slide 22
Challenge: higher-level abstractions
  grid-specific communication protocols (e.g., high reliability data dissemination) enabled via SDN
  high-level data distribution abstractions:
    publish-subscribe [Gridstat, NASPInet]
    data-gathering + analytics: closed-loop cyber-physical system
  network virtualization: one physical network to home carrying multiple logically separate networks?
    smart-grid, security, entertainment
multicast
QoS tree
X
multicast
QoS tree
healed

## Slide 23: Overview
yesterday’s, today’s and tomorrow’s electric grid: a networking perspective
five (networking) smart grid challenges
  richer data gathering and distribution architecture
  monitoring, measurement
  dealing with demand: network-inspired approaches
  security and privacy
  power routing
grid v. Internet: similarities and dis-similarities
  reflections on Keshav’s 1st and 2nd hypotheses

## Slide 24: Control plane: measurement
transmission network
(backbone)
distribution
network (edge)
distribution
network
operator(s)
regional
transmission
operator(s)
large-scale
electricity
generators
monitoring
control
Monitoring, control
monitoring, control
Phasor Measurement Units (PMUs)
Intelligent electronic devices (IED)
Advanced Metering Infra. (AMI)

## Slide 25: Grid measurement/monitoring
where to place measurement devices to maximize observability?
Observability rule 1: if PMU placed at a, then a and its neighbors are observable
Observability rule 2: if a node is observable and all but one neighbors are observable, then all neighbors observable
D. Brueni and L. Heath. The PMU Placement Problem. SIAM Journal on Discrete Math, 2005
MaxObserve: Given graph, G=(V,E) and k PMUs, place k PMUs to maximize number of observed nodes
  MaxObserve is NP-complete, Reduce from Planar 3SAT (P3SAT)

## Slide 26: PMU placement with cross validation
where to place measurement devices to maximize measurement cross validation?
Observability rule 3: If PMUs placed on adjacent nodes, they cross-validate each other
Observability rule 4: If two PMUs share a common neighbor, the two PMUs cross-validate each other
Vanfretti et al. A Phasor-data-based State Estimator Incorporating Phase Bias Correction. IEEE Transactions on Power Systems, 2010
MaxObserve-XV: Given graph, G=(V,E) and k PMUs, place k PMUs to maximize number of observed nodes, requiring that all PMUs be cross-valided
  MaxObserve-XV is NP-complete,
a
b
a
c
b
PMU
PMU
PMU
PMU

## Slide 27: Greedy Solutions to PMU placement
MaxObserveGreedy: iteratively place k PMUs: iteratively at node that results in observation of max # new nodes
MaxObserveGreedy-XV: iteratively place PMU pairs at nodes{u,v}, such that u and v are cross-validated and result in observation of max #new nodes
  evaluation:
    generate grid networks with same degree distribution as IEEE Bus 57
    brute force optimal solution by enumeration for small # PMUs

## Slide 28: Greedy Solutions: evaluation
MaxObserveGreedy within 98.6% of optimal
MaxObserveGreedyXV within97% of optimal
cross-validation requirement on decreases # observed nodes by ~ 5%
D. Gyllstrom, E. Rosensweig, J. Kurose, “On the Impact of PMU Placement on Observability and Cross-Validation,” Proc. ACM e-Energy 2012

## Slide 29: Overview
yesterday’s, today’s and tomorrow’s electric grid: a networking perspective
five (networking) smart grid challenges
  richer data gathering and distribution architecture
  monitoring, measurement
  dealing with demand: network-inspired approaches
  security and privacy
  power routing
grid v. Internet: similarities and dis-similarities
  reflections on Keshav’s 1st and 2nd hypotheses

## Slide 30: Dealing with demand
computer network:
packet-level congestion
local
reactive: buffer, defer load
smart grid network:
balancing power supply, demand
global
reactive: load, source shedding
proactive: buffering via storage
  pumped hydro, battery
  prediction crucial

## Slide 31: SmartCharge: residential battery storage
Key idea: charge battery at off-peak hours
  off-peak price < peak price
  shift residential grid use from peak to off peak hours: charge battery when prices are low, use battery (reducing grid use) when prices are high
0
0.02
0.04
0.06
0.08
0.1
0.12
12am
7am
11am
5pm
7pm
11pm
Hourly Rate ($/kwH)
Hour of Day
Illinois Real-time
0
2.5
5
7.5
12am
7am
11am
5pm
7pm
11pm
Grid Power (kW)
Hour of Day
Without SmartCharge
With SmartCharge (12kWh)
Notes: Flip ordering of smartcharge and smartcap. Complementary. Bring back problem statement. ACM e-Energy 2012, ACM BuildSys 11
Go back to pricing.
Limitations to how much we can do with smartcap.
  Solar panel can do the same thing.
Use energy storage as buffer
  Analagous to how people have used buffers to smooth out traffic.
  Put ACM e-Energy reference.
I’ll first discuss smartcharge, which takes advantage of utilities adopting variable pricing.
The economics of power generation I described earlier make the real-time cost of power differ as demand rises and falls----other factors contribute as well (congested transmission lines, excess demand).
However, most utilities still use fixed-rate pricing that just charges a fixed amount per kWh (or tiered). Even though it costs utilities more to generate electricity at peak times, consumers have no incentive to decrease use during those times. Variety of pricing plans that utilities are trying out: TOU (ontario). Real-time (illinois) (Rod Blagoyavich). Peak-load pricing ( ). In many cases, the off-peak prices can be up to 5X lower than the peak prices.

## Slide 32: SmartCharge: Charging-Discharging Decision
given: electricity price from day-ahead market
predict: consumption
compute: optimal battery charge/discharge schedule
SmartCharge Optimizer (LPF)
Electricity Prices
(known)
Next Day Demands
(predict)
When & how much to Charge Battery
When & how much to Discharge Battery
Inputs
Outputs
compute

## Slide 33: Demand prediction via machine learning
predict future energy usage, training using past historical data
  data features:
    weather (temperature + humidity)
    time (month, day, weekend, holiday)
    history (previous day)
best predictions with SVM-Poly
  within 5.75% of real usage
  best at night (within 4%)
Notes: Flip ordering of smartcharge and smartcap. Complementary. Bring back problem statement. ACM e-Energy 2012, ACM BuildSys 11
Lots of approaches. Over TOU periods from Toronto.
I’ll first discuss smartcharge, which takes advantage of utilities adopting variable pricing.
The economics of power generation I described earlier make the real-time cost of power differ as demand rises and falls----other factors contribute as well (congested transmission lines, excess demand).
However, most utilities still use fixed-rate pricing that just charges a fixed amount per kWh (or tiered). Even though it costs utilities more to generate electricity at peak times, consumers have no incentive to decrease use during those times. Variety of pricing plans that utilities are trying out: TOU (ontario). Real-time (illinois) (Rod Blagoyavich). Peak-load pricing ( ). In many cases, the off-peak prices can be up to 5X lower than the peak prices.

## Slide 34: SmartCharge: LPF
Min cost with battery storage for ToU pricing
1. Objective
2. Energy charged >= 0
3. Energy discharged >= 0
4. Max charging rate
5. Charge conservation
6. Capacity constraint
7. Price calculation

## Slide 35: SmartCharge: Household Savings
  10-15% savings
  within 8-12% of Oracle
  savings flatten >24kWh
A. Misra, D. Irwin, P. Shenoy, J. Kurose, T. Zhu, “SmartCharge: Cutting the Electricity Bill in Smart Homes with Energy Storage,” Proc. ACM e-Energy 2012
Notes: Motivation for peak load reduction and demand-side energy management. Instrumented 3 homes to conduct research. Present deployment (most instrumented).
SmartHome prototype
SmartCharge
Take Insteon switches with me. Works like a normal switch. You can query it. How much power are you drawing. You can toggle the switch.
Other homes instrumented to varying degrees. NEST thermostat. Thermostat can learn. My home is the most instrumented.
Building smart home lab at UMass. Show some live data.
We can control switches, outlets, thermostats
Monitor devices: interrupts vs. polling
We use multiple different types of technology: Insteon (powerline, wireless), Zwave, HomePlug,
Utilities are rolling out smart meters. Not as advanced as the ones in my panel, but they will get there.
Lots of analytics you could think about doing.
Use as a tool for teaching. Sean controlling stuff in my basement.
Keep you honest about implementing these techniques.
Learn interesting engineering issues related to scale, fidelity, granularity of sensors and network. Getting highly accurate readings over low-bandwidth wireless/powerline links for lots of devices.
Use data for a lot of other projects as well.
Take advantage of mature sensing products. Get lot of redundant data that we want to correlate and process.

## Slide 36: Prediction: many opportunities
home demand
peak demand flattening (via shiftable loads, storage)
renewable sources (wind, hydro) generation
transmission grid demand
…..

## Slide 37: Overview
yesterday’s, today’s and tomorrow’s electric grid: a networking perspective
five (networking) smart grid challenges
  richer data gathering and distribution architecture
  monitoring, measurement
  dealing with demand: network-inspired approaches
  security and privacy
  power routing
grid v. Internet: similarities and dis-similarities
  reflections on Keshav’s 1st and 2nd hypotheses

## Slide 38: Security and Privacy
many Internet analogies (indeed, communication infrastructure needs to be protected)
securing infrastructure
securing data
  protection from eavesdroppers
  detecting injection attacks
privacy: randomized AMI to allow accurate aggregate load prediction, while maintaining individual privacy

## Slide 39: Overview
yesterday’s, today’s and tomorrow’s electric grid: a networking perspective
five (networking) smart grid challenges
  richer data gathering and distribution architecture
  monitoring, measurement
  dealing with demand: network-inspired approaches
  security and privacy
  power routing
grid v. Internet: similarities and dis-similarities
  reflections on Keshav’s 1st and 2nd hypotheses

## Slide 40: Electric grid: sources, destinations
transmission network
(backbone)
distribution
network (edge)
power flows not distinct, not addressable (no packet headers)
traditionally: power passively flows following Kirchoff’s and Ohm’s laws(no “active” routing)
Observation: transmission networks move power from
sources to destinations - seems analogous to routing!

## Slide 41: Electric grid: power routing
transmission network
(backbone)
FACTS (flexible AC transmission system) devices – dynamically change transmission line impedance, changing passive power flow!
distribution
network (edge)
X12
X13

## Slide 42: Power routing
Si: source (generated) flow at i
Li: load (consumed) flow at i
Xij: flow from node i to node j
Find Xij to minimize some cost function of Xij subject to:
  flow conservation (flow in = flow out)
  capacity constraints (Xij < Cij)
Routing algorithms are the “bread and butter” of networking researchers
i
j
Xij

## Slide 43: Overview
yesterday’s, today’s and tomorrow’s electric grid: a networking perspective
five (networking) smart grid challenges
  ultra-reliable, multi-destination transport
  monitoring, measurement
  security and privacy
  dealing with demand: network-inspired approaches
  power routing
grid v. Internet: similarities and dis-similarities
  reflections on Keshav’s 1st and 2nd hypotheses

## Slide 44
What can the smart grid learn from 40 years of computer networking research?

## Slide 45: Grid versus Internet: network of networks
low degree of inter-RTO connectivity (rather than dense connectivity)
geographic proximity determines RTO connectivity (rather than peering,
customer-provider relationships)
distribution network connects to single RTO (albeit at multiple points for redundancy)
Q: Regional transmission network == Autonomous System
?
A: analogy is a bit strained

## Slide 46
Reflection: what can the Internet teach us?
similarities (on the surface):
  power routing = internet flow routing
  AS == RTO
  grid management = network management
Internet technologies, research developed over
past 40 years, can be used to green the grid
Keshav 1st hypothesis
but….
  Internet best effort service model won’t cut it
  manageability, security, reliability (five 9’s) not yet Internet main strengths
The “sweet spot” is in developing
the control plane architecture!

## Slide 47
Reflection: what can the Internet teach us?
architecture: punctuated equilibrium?
today’s IP v4: 30+ years old
telephone network: manual to stored-program-control to IP over 100 years
today’s meteorological sensing network: 30+ years old
The next decade will determine the structure of the grid in 2120
Keshav 2nd hypothesis
…… the time is indeed now

## Slide 48: Conclusions
smart grid: many research opportunities
ICT can/must inform smart grid design operation
importance of working with domain experts
  two-way collaboration with significant “start up” costs, e.g., bioinformatics, sense-and-response hazardous weather prediction
IITB/Umass joint seminar: spring 2013

## Slide 49
the end
- thank you -
?? || /* */